BHARATI RESEARCH STATION — SHORT TECHNICAL NOTES

SIH Research Reference

1. LOCATION & ENVIRONMENT

• Location: Larsemann Hills, Ingrid Christensen Coast, Princess Elizabeth Land, Antarctica.

• Located between Thala Fjord and Quilty Bay, east of Stornes Peninsula.

• Relatively ice-free rocky oasis bordering Prydz Bay.

• Operational area: ~2 km².

• Elevation: ~35 m above mean sea level.

• Nearby stations: Russian Progress Station and Chinese Zhongshan Station.

• Main physical access: Austral Summer (November–February).

• Winter isolation: April–October.

2. MAIN BUILDING — STRUCTURAL DETAILS

• Dimensions: 53.230 m (L) × 30.200 m (W) × 16.294 m (H).

• 134 prefabricated shipping containers.

• Total weight: 401.551 tonnes.

• Foundation: 83 GEWI injection piles.

• Wind loading: 54.3 psf dynamic gust pressure.

• Design life: ≥25 years.

• Building is elevated to reduce snow accumulation.

• Thermal envelope: PU-core steel sandwich panels.

• Windows: multi-cavity inert-gas glazing.

• Window heat-transfer coefficient: 0.6 W/(m²·K).

3. CONSTRUCTION & HISTORY

• 2006–2009: Architectural planning/design by consortium including bof Architekten, IMS Ingenieurgesellschaft and m+p consulting.

• 2010–2012: Construction; 134 containers prefabricated in Germany and shipped via Antwerp and Cape Town.

• 18 March 2012: Official commissioning.

• 2013: TechBean Systems Pvt. Ltd. involved in BMS O&M.

• 2014–2015: ISRO/NRSC established AGEOS at Bharati.

• 2016–2017: Mangala Mani became ISRO's first woman scientist to winter over at Bharati, spending 403 days in Antarctica.

• 2022: Indian Antarctic Bill established a domestic legal framework for Indian Antarctic operations.

4. BUILDING LAYOUT

GROUND FLOOR — LEVEL 1

• Laboratories

• Cold storage

• Technical workspaces

• Workshop

• Electrical infrastructure

FIRST FLOOR — LEVEL 2

• 24 single/double bedrooms

• Kitchen

• Dining room

• Library

• Fitness room

• Sauna

• Administrative offices

• Lounge

• Medical operating theatre

SECOND FLOOR — LEVEL 3 / TERRACE

• Local HVAC systems

• Scientific experiments

• Observation equipment

5. POWER GENERATION

• 3 × 100 kVA CHP generators.

• Fuel: Jet A-1.

• Total installed electrical capacity: 300 kVA.

• CHP waste heat is recovered through heat exchangers and used for station heating.

• Approximate indoor temperature: ~20°C.

• External temperatures can reach ~−40°C.

• Maximum thermal demand: 155 kWth.

• Heating system: low-temperature glycol-water circulation network.

• Heat source: recovered CHP waste heat.

POWER DISTRIBUTION

• Air Circuit Breaker: 3-pole.

• ETU20 LSIN.

• Rating: 250 A.

• Breaking capacity: 55 kA / 415 V AC.

UPS

• 2 × 60 kVA UPS systems support the Main Low Voltage Distribution system.

• Note: another source entry mentions 260 kVA UPS; this should be verified before final use.

6. POWER CONTROL & LOAD SHEDDING

• Distributed Control System (DCS) manages electrical loads.

• If a generator fails, critical systems receive priority:

- HVAC

- Water-pipe trace heating

- Communications

- Life-support systems

• Non-essential systems can be disconnected:

- Sauna

- Recreation

- Other non-critical zones

IMPORTANT POWER DATA

• Generator RPM

• Oil pressure

• Exhaust temperature

• Electrical load

• Voltage/current/frequency

• Fuel consumption

• UPS status

• Breaker status

7. HVAC & AIR QUALITY

• HVAC is automated through the BMS.

• Air Handling Units (AHUs) provide:

- Fresh air

- Heating

- Humidification

• CO and CO₂ sensors installed at critical locations.

AUTOMATION

• High CO₂ → increase ventilation/fresh-air intake.

• Good air quality → reduce outside-air intake to conserve heating energy.

IMPORTANT HVAC DATA

• Temperature

• Humidity

• CO

• CO₂

• Airflow

• Fan status

• Heating demand

• AHU status

8. WATER SUPPLY & DESALINATION

• Seawater desalination system uses Quilty Bay.

• Intake depth: ~12 m to avoid surface ice.

• Pump house: dedicated 10-ft container near shoreline.

• Pipeline from pump house to main building: ~300 m.

• Pipeline is insulated and protected by electrical trace heating.

CRITICAL FAILURE CHAIN

Trace-heating failure

→ Pipe freezes

→ Seawater supply stops

→ Desalination stops

→ Drinking/sanitation water affected

IMPORTANT MONITORING

• Trace-heating current

• Trace-heating resistance

• Pipeline temperature

• Pump status

• Water flow

• Water pressure

• Tank levels

• Desalination status

9. FUEL INFRASTRUCTURE

JET A-1

• Used mainly for CHP generators.

• Fuel farm capacity: 296 kL.

• Transfer distance: ~350 m.

• Transfer frequency: every 8–10 days.

• Intermediate storage tank: 13.6 kL.

• Day tank: 470 L.

• Day tank automatically feeds the power station.

FUEL MONITORING

• Tank level

• Fuel consumption

• Transfer status

• Pump status

• Leakage

• Tank temperature

• Daily burn rate

• Predicted remaining operating days

POLAR DIESEL

• Used mainly for:

- Tracked vehicles

- Snowmobiles/snow scooters

- Other land transportation

10. WASTE MANAGEMENT

SOLID WASTE

• Compacted.

• Securely stored.

• Returned to India during summer resupply.

WASTEWATER/SEWAGE

• Treated internally.

POSSIBLE MONITORING

• Tank levels

• Flow rates

• Treatment status

• Pump status

• Leakage

• Remaining waste capacity

11. BUILDING MANAGEMENT SYSTEM — BMS

• Approximately 1,000 monitoring/control data points.

• TechBean Systems Pvt. Ltd. involved in O&M since 2013.

• Technologies/protocols mentioned:

- SCADA

- PLC

- Modbus

- IEC 60870-5

MAJOR BMS SUBSYSTEMS

• Water Leak Detection (WLD)

• Fire alarm

• Fire suppression

• CCTV

• Access control

• Rodent-repellent systems

12. SATELLITE GROUND STATION — AGEOS

• AGEOS = Antarctica Ground Station for Earth Observation Satellites.

• Operationalized by ISRO/NRSC around 2014–2015.

• Communication bands:

- S-band

- X-band

• Tracks polar-orbiting satellites.

• Receives Earth-observation data.

• Data is buffered and transmitted to NRSC, Hyderabad.

13. SCIENTIFIC MONITORING

Research/monitoring includes:

• Black Carbon aerosols

• Climate indices

• Historical weather patterns

• Seismological data

• Magnetic data

• Meteorological observations

NPDC DATASETS MENTIONED

• AWS Data — Bharati Station

• Synoptic Data from Bharti Station (2016–21)

• Black Carbon datasets

AWS DATA

• Temperature

• Pressure

• Wind

14. PERSONNEL CAPACITY

SUMMER

• Maximum capacity: ~72 personnel.

• Main building: 47.

• Emergency summer shelters: 25.

WINTER

• Approx. 24 overwintering personnel.

• Essential roles:

- Scientists

- Medical staff

- Cooks

- Mechanical/electrical personnel

HUMAN FACTOR

Winter isolation may cause:

• Circadian disruption

• Sleep problems

• Reduced concentration

• Cognitive fatigue

• Reduced decision-making performance

DIGITAL UI REQUIREMENT

• Simple navigation

• High contrast

• Clear icons

• Minimal steps

• Automation

• Prominent critical alarms

• Low cognitive load

15. LOGISTICS & AVIATION

SUPPLY CHAIN

Cape Town

→ Antarctic waters

→ Expedition vessel

→ Helicopter

→ Bharati

• Heavy cargo, fuel and equipment mainly transported during summer.

• Heavy-lift helicopter: KAMOV-32 or equivalent.

• Coaxial rotor design supports stable underslung cargo operations.

• Expedition vessel helideck: 16 × 16 m.

HELIPADS

• Total: 3

- 2 concrete

- 1 wooden

• Main helipad: ~900 m².

• Adjacent fueling facility.

16. GROUND TRANSPORT

VEHICLES

• PistenBully 300

• Tracked polar vehicles

• Snowmobiles

• Snow scooters

• Modified Toyota Hilux pickup trucks

USES

• Cargo movement

• Personnel movement

• Station-area logistics

• Field operations

17. MEDICAL & EMERGENCY CAPABILITY

• Medical operating theatre available.

• Winter evacuation is extremely difficult/impossible under severe isolation/weather.

• Requires adequate:

- Medical supplies

- Spare parts

- Emergency equipment

- Power redundancy

- Communication redundancy

• Notes mention a maritime incident involving ~100 passengers evacuated to Bharati, demonstrating summer emergency/mass-casualty capability.

18. MAINTENANCE & SPARE PARTS

• O&M governed by multi-year government contracts.

• TechBean Systems Pvt. Ltd. involved with BMS O&M since 2013.

• NCPOR OMRC tender: AL-11019/1/2025.

• Normal spare-part delivery is unavailable during winter.

• Spare-part and inventory management are therefore critical.

KEY CHALLENGE

Equipment failure during winter

→ No immediate external supply

→ Dependence on onboard spare parts

→ Local repair capability required

19. CURRENT DIGITAL ECOSYSTEM

CURRENT FLOW

Sensors

→ PLC/SCADA

→ BMS

→ Local alarms/control

• Approximately 1,000 data/control points.

• Data is heavily localized.

• Remote headquarters visibility may be fragmented.

• Potential improvement: unified real-time command-and-control dashboard.

20. PROPOSED DIGITAL PLATFORM

A. SEAWATER INTAKE PREDICTIVE MAINTENANCE

Monitor:

• Current

• Resistance

• Pipe temperature

• Water flow

• Pump status

ML anomaly detection:

• Detect abnormal electrical behavior.

• Predict trace-heating failure.

• Warn before pipeline freezing.

B. GENERATOR PREDICTIVE MAINTENANCE

Monitor:

• RPM

• Oil pressure

• Exhaust temperature

• Electrical output

• Fuel consumption

• Operating hours

Purpose:

• Detect component degradation.

• Predict maintenance requirements.

• Reduce unexpected winter failures.

C. HVAC OPTIMIZATION

Combine:

• Indoor CO/CO₂

• HVAC data

• External AWS/weather data

• Temperature

• Wind

• Occupancy

Purpose:

• Predict heating demand.

• Optimize HVAC.

• Reduce Jet A-1 consumption.

D. FUEL BURN-RATE MODELING

Track:

• Current fuel level

• Daily consumption

• Consumption trend

• Remaining operating days

• Transfer frequency

• Predicted resupply requirement

Track separately:

• Jet A-1

• Polar Diesel

21. OFFLINE-FIRST ARCHITECTURE

PROBLEM

Communication may be disrupted because of:

• Weather

• Satellite availability

• Solar conditions

• Limited bandwidth

RECOMMENDED ARCHITECTURE

Sensors

→ Local Edge Gateway

→ Local Database/AI

→ Local BMS Actions

→ Connectivity returns

→ Data synchronization

→ NCPOR/Goa

KEY PRINCIPLE

Safety-critical operations must continue even when cloud/remote connectivity is unavailable.

22. SECURITY & ACCESS CONTROL

USE RBAC — ROLE-BASED ACCESS CONTROL

Possible roles:

• Scientists

• Engineers

• Medical staff

• Administrators

• Station commander

• Remote NCPOR operators

CRITICAL MANUAL OVERRIDE SHOULD RECORD:

• User ID

• Timestamp

• Action

• Previous state

• New state

• Reason

Then generate:

• Immutable audit log

• Remote alert

23. IMPORTANT SENSOR/DATA CATEGORIES

POWER

• RPM

• Oil pressure

• Exhaust temperature

• Voltage

• Current

• Frequency

• Power output

• Fuel consumption

• UPS status

• Breaker status

HVAC

• Temperature

• Humidity

• CO

• CO₂

• Airflow

• Fan status

• Heating demand

• AHU status

WATER

• Intake temperature

• Pipeline temperature

• Trace-heater current

• Trace-heater resistance

• Pump status

• Flow

• Pressure

• Tank level

• Desalination status

FUEL

• Tank level

• Flow rate

• Transfer pump status

• Consumption

• Leakage

• Tank temperature

BUILDING

• Water leaks

• Fire/smoke

• Door/access status

• CCTV status

• Server-room conditions

• Equipment alarms

WEATHER

• Temperature

• Wind speed

• Wind direction

• Atmospheric pressure

• Other AWS parameters

24. KEY NUMBERS — QUICK REVISION

• Operational area: ~2 km²

• Elevation: ~35 m AMSL

• Building: 53.230 × 30.200 × 16.294 m

• Containers: 134

• Building weight: 401.551 tonnes

• Foundation: 83 GEWI piles

• Design life: ≥25 years

• CHP generators: 3 × 100 kVA

• Total CHP capacity: 300 kVA

• Thermal demand: 155 kWth

• UPS: 2 × 60 kVA

• BMS data points: ~1,000

• Seawater intake depth: ~12 m

• Intake pipeline: ~300 m

• Jet A-1 fuel farm: 296 kL

• Intermediate fuel tank: 13.6 kL

• Day tank: 470 L

• Fuel transfer distance: ~350 m

• Fuel transfer interval: 8–10 days

• Summer capacity: ~72

• Winter crew: ~24

• Main building summer capacity: 47

• Emergency summer shelters: 25

• Main helipad: ~900 m²

• Helipads: 3

• Expedition vessel helideck: 16 × 16 m

• Indoor target temperature: ~20°C

• External temperature mentioned: ~−40°C

• Window heat-transfer coefficient: 0.6 W/(m²·K)

25. HIGHEST-PRIORITY DIGITAL MONITORING AREAS

1. Seawater trace heating — prevent water-supply failure.

2. CHP generators — predictive maintenance.

3. Fuel tanks/farm — consumption and remaining-days prediction.

4. HVAC — energy optimization.

5. Power/DCS — generator failure and load prioritization.

6. Fire/water-leak detection — infrastructure protection.

7. Inventory — winter spare-parts management.

8. Personnel/medical — emergency readiness.

9. Weather/AWS — operational decision support.

10. AGEOS/communications — connectivity and satellite operations.

11. Security/RBAC — prevent unauthorized critical-system changes.

12. Offline edge computing — autonomous operation during communication loss.